## Slide 1: Critical Infrastructure Security: The Emerging Smart Grid In Class: Cpt S 580-03, Cpt S 483-01, EE 582-02, EE 483-01 Online or Tri-Cities: Cpt S 580-03, Cpt S 483-01, Cpt S 483-02, EE 582-01, EE 483-01
Dr. Anurag K. Srivastava, Dr. Carl Hauser, Dr. Dave Bakken,
and Dr. Min Sik Kim
Computation Lecture 6: Grid Wide Area Measurement Systems

## Slide 2: Today’s Content
Introduction
Emerging Power Applicaions
Implementation Issues for WAMS Data Delivery (WAMS-DD)
NASPI and NASPInet
GridStat
Lots to cover, not in full detail in every area
Main reading here is the Proceedings of the IEEE paper listed in Lecture 1 of this computation segment

## Slide 3: Background: Applied Computer Scientist
Work in “distributed computing”, above the network layer
  Not a power engineer!
Working closely with Prof. Anjan Bose for 13 years.
  “How can distributed computing (and computer networking and real-time computing) help improve communications for the bulk power grid?”
  Also Mani Venkatasubramanian (power), Carl Hauser (distributed computing)
1990s at research lab BBN working on wide-area data delivery for DARPA
Worked for Boeing, consulted to Amazon.com , etc.

## Slide 4: Better Communications are Needed
Grids are getting more stressed each year
  “With the exception of the initial power equipment problems in the August 14, 2003 blackout [in North America], the on-going and cascading failures were almost exclusively due to problems in providing the right information to the right place within the right time.”
  Francis Cleveland, 2007
Inadequate communications major contributing factor in recent major blackouts
Other challenges for the bulk power system
  Growth in generation and load far more than transmission capacity growth (in North America)
  Integrating renewable sources of energy
  Distributed control
  Retiring operators (in North America)
All can be mitigated by better communications

## Slide 5: Communications & Application Interoperability
Interoperability (“universal connectivity”) is key
  In order to create this new power delivery system, what is needed is a national electricity-communications superhiway …. The ultimate challenge in creating the power delivery system of the 21st century is in the development of a communications infrastructure that allows for universal connectivity.
  Clark Gellings, US EPRI, 2003 (emphasis is mine)
This interoperability (“universal connectivity”) can only be achived at the data/middleware layer, not the network layer
  See our Grid-Interop 2009 paper for more (details at end)

## Slide 6: Today’s Content
Introduction
Emerging Power Applicaions
Implementation Issues for WAMS Data Delivery (WAMS-DD)
NASPI and NASPInet
GridStat

## Slide 7: Wide Range of QoS+ Requirements
QoS+:
  network/middleware “QoS” (latency, rate), availability/criticality
  Also things an implementer/deployer of WAMS-DD needs to know: geographic scope, quantity.
Comparing Apples and Apples:
  Normalize each from 1 (very easy) to 5 (very hard)
Wide ranges
  Across application families
  Sometimes within them (each configuration is different)

## Slide 8
Difficulty (5 : hardest) | Latency (msec) | Rate (Hz) | Criticality | Quantity | Geography | Deadline (for Bulk)
5 | 5–20 | 240–720+ | Ultra | Very High | Across grid or multiple ISOs | <5 sec.
4 | 20–50 | 120–240 | High | High | Within an ISO/ RTO | 1 min.
3 | 50–100 | 30–120 | Medium | Medium | Between a few utilities | 1 hr.
2 | 100–1000 | 1–30 | Low | Low | Within a single utility | 1 day
1 | >1000 | <1 | Very Low | Very Low (serial) | Within a substation | >1 day
Also what kind of msgs (both I/O): streaming, condition-based, bulk; person or computer in loop
Normalized Values of QoS+ Parameters

## Slide 9: Applications (ProcIEEE Section & NASPInet Class)
Traditional State Estimation (III.A)
Direct State Measurement (III.A & NASPInet Class B)
Operator Displays (III.B & NASPInet Class D)
Catch Up For Operator Displays (III.B)
Distributed Wide-Area Control (NASPInet Class A)
Distributed SIPS (III.C & NASPInet Class A)
Synchronous Distributed Control (III.C & NASPInet Class A)
Renewable Generation Islanding Control
Transient Stability (III.C & NASPInet Class A)
Ancillary Services (III.C & NASPInet Class A)
Automated Contingency Drill-Down (III.D & NASPInet Class D, sort of)
Post-Event Analysis (III.E & NASPInet Class C)
Research Traffic (III.F & NASPInet Class E)
This normalized parameterization can be considered a (significant) refinement of the original NASPInet traffic categories
Can’t go through following tables in great detail due to time
Bottom line: Wide range of QoS+ requirements; not “one size fits all”

## Slide 10: Most Difficult Input for Each App
App | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
Loop Entity | P | P | P | P | C | C | C | C | C | C | P | P | P
Kind | SS | SS | SS | Co | SS | SS | SS | SS | SS | SS | SS | Co | Co
Lat. | 1–2 | 1–2 | 1 | 1 | 2–4 | 4–5 | 2–4 | 2-3 | 5 | 1 | 1 | 1 | 1
Rate | 1–2 | 1–2 | 2–3 | — | 2–3 | 5 | 1-2 | 2–3 | — | — | 2–3 | — | —
Crit | 1-5 | 1-5 | 1-5 | 1–2 | 5 | 5 | 5 | 4-5 | 5 | 1–3 | 5 | 1-5 | 1-5
Quan | 3–5 | 1–2 | 3–5 | 1–2 | 3–5 | 2–4 | 1-3 | 1-3 | 1–2 | 1–5 | 3–5 | 5 | 1-5
Geog | 5 | 1-5 | 5 | 5 | 1–5 | 1–5 | 1–5 | 2-3 | 4-5 | 3–5 | 3–4 | 3–5 | 3–5
Dline | — | — | — | 5 | — | — | — | — | — | — | — | 2–3 | 1
Notice: very wide range of parameters
  …….. And this is just for applications conceived today, let alone the 30+ year expected lifetime of NASPInet

## Slide 11: Most Difficult Output for Each App
App | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
Loop Entity | P | P | P | P | C | C | C | C | C | C | P | P | P
Kind | SS | SS | SS | Bu | Co | Co | Co | Co | Co | SS | SS | Bu | Bu
Lat. | 1–2 | 1–2 | 1 | — | 3-5 | 5 | 3-5 | 3–5 | 5 | 1–2 | 1 | — | —
Rate | 1–2 | 1–2 | 1 | — | — | — | — | — | — | 1–2 | 2–3+ | — | —
Crit | 3 | 3 | 3 | 1–2 | 5 | 5 | 5 | 5 | 5 | 1–3 | 5 | 1–2? | 1
Quan | 3–5 | 1–2 | 1 | 2–4 | 1-2 | 1 | 1 | 1 | 1 | 1 | 3–5 | 5 | 5
Geog | 1–2+ | 1–3+ | 1 | 1–2+ | 1–5 | 1–5 | 1–5 | 2-3 | 3–5 | 2 | 3–4 | 5 | 5
Dline | — | — | — | 5 | — | — | — | — | — | — | — | 2–3 | 1
Notice: very wide range of parameters
  …….. And this is just for applications conceived today, let alone the 30+ year expected lifetime of NASPInet

## Slide 12: Today’s Content
Introduction
Emerging Power Applicaions
Implementation Issues for WAMS Data Delivery (WAMS-DD)
NASPI and NASPInet
GridStat

## Slide 13: QoS Requirements
Latency
  4 ms within substation, 8-12+
Rate (1/minute to 250/second)
Availability of Data (EPRI IntelliGrid 2004)
Level | Availibility (%) | Downtime/Year
Ultra | 99.9999 | ~ ½ second
Extremely | 99.999 | ~5 minutes
Very | 99.99 | ~1 hour
High | 99.9 | ~9 hours
Medium | 99.0 | ~3.5 days
Delivered QoS must be tailorable per data item & changeable (in SW)
Notes: 14

## Slide 14: Internet vs. NASPInet environment
Characteristic | Internet | EPInet
Network size | 109 interconnected hosts worldwide | 105 hosts in a power grid 103-4 “routers”
Per-Flow state? | Death (RSVP) | Very feasible
Network design goal | Provide best-effort delivery for any user and purpose | Provide guaranteed QoS in several dimensions for specific users and purposes
Admission Cntl Perimeter | None | Complete
Fraction of Managed Traffic | None/Very Little | Almost all. All traffic subject to policing. >>90% periodic.
Central topology knowledge | Not attempted, because of large scale and dynamicity | Feasible, because of small scale and slow changes
Topology changes (!failure) | Often & without warning | Not often & virtually always with warning (except failure)
Frequency of route changes | Frequent; route changes computed using distributed algorithms that may converge slowly in the face of changing topology | Infrequent; route changes computed centrally assuming stable topology
Notes: 16

## Slide 15
Characteristic | Internet | NASPInet
Latency Level Achievable | Slow to Medium | Very Fast
Latency Predictability | Poor | Very Good to Excellent
Recovery delay after dropped packet (with “reliable” delivery) | High (timeout waiting for data or acknowledgement) | Zero (redundant copy sent over disjoint path arrives virtually at the same time) DO NOT USE post-error recovery, be proactive!
Forwarding Unit | Uninterpreted packet | Update of a variable
Traffic Predictability | Low | Very High
Elasticity of QoS requirements | None/Low | Medium-High
Multicast: multiple subscribers to a single update flow | A small fraction of the overall traffic; does not justify significant optimization | The common case. Multiple subscribers to a single update flow may have different latency and reliability requirements. Significant opportunity for optimization.
Internet vs. NASPInet environment (cont.)
Notes: 17

## Slide 16: Today’s Content
Introduction
Emerging Power Applicaions
Implementation Issues for WAMS Data Delivery (WAMS-DD)
NASPI and NASPInet
GridStat

## Slide 17: Synchrophasors
SCADA (1960s technology) provides
  Slow updates (2-4 seconds)
  Crude: polling architecture, no QoS, little cyber-security
  Clocks at sensors can be highly unsynchronized
Phasor Measurement Units (PMUs)
  Idea around for a few decades (Phadke)
  Practical recently with cheap GPS chips, etc
  Measure voltage, current, frequency, …. with microsecond accuracy
  Lets industry move from (nonlinear) “state estimation” towards direct “state measurement”

## Slide 18: Actual Example – Aug. 14th, 2003 Blackout
  According to NERC, “A valuable lesson from the August 14 blackout is the importance of having time-synchronized system data recorders. NERC investigators labored over thousands of data items to synchronize the sequence of events. … That process would have been significantly improved … if there had been a sufficient number of synchronized data recording devices.”
Notes: Time synchronized, precise measurements – one example of this kind of benefit

## Slide 19: NASPI
Vision: “The vision of the North American SynchroPhasor Initiative (NASPI) is to improve power system reliability through wide-area measurement, monitoring and control.”
  Synchrophasor: a sensor with a very accurate GPS clock…
  Becoming much more deployed in US, Europe, …
Great need for much better data delivery services
  Can no longer send “all data to control center at the highest rate anyone might want to”
Very involved with spec of “NASPInet”
  Many requirements come from GridStat research (cited)
Notes: 32

## Slide 20: NASPInet Conceptual Architecture
Notes: 5

## Slide 21: Today’s Content
Introduction
Emerging Power Applicaions
Implementation Issues for WAMS Data Delivery (WAMS-DD)
NASPI and NASPInet
GridStat

## Slide 22: GridStat Architecture

## Slide 23: Route Allocation to Subscriber 1
Subscriber 1
Publisher 1
Publisher 3
Publisher 2
Note: GridStat, not app programmer, figures route/path

## Slide 24: Route Allocation to Subscriber 2
Subscriber 1
Publisher 1
Publisher 3
Publisher 2
Note: Sub2 may have different latency, rate, #paths than Sub1
Subscriber 2

## Slide 25: Overview of GridStat Performance
Forwarding Latency through one status router between ~50 microseconds (20010 vintage PC)
  Very little jitter
  Scales to 300-500K+/sec in Java
  Even much faster with “network processors”
  In custom HW should scale about same as IP router
So forwarding across an entire grid would be less than a millisecond over the speed of light
  8-10 hops over a wider area would be typical
  You can afford a millisecond (IMHO; YMMV)
You cannot buy COTS products that give you the complete required flexiblity and QoS control (including rate filtering)

## Slide 26: Conclusions
Better WAMS-DD can help the bulk power system
WAMS-DD has more extreme requirements than any other; need to be careful here
NASPInet is an encouraging conceptual network for WAMS-DD
GridStat was designed from the ground up to do WAMS-DD
  Most full-featured NASPInet Data Bus implementation available