## Slide 1: Digital Systems for the Smart Grid Computation Segment Lecture 2: Data Management and IEC 61850
Dr. Anurag K. Srivastava,
Dr. Carl Hauser,
Dr. Dave Bakken,
Dr. Min Sik Kim
Washington State University

## Slide 2: Today’s Content
Background
UML
XML
RDF
CIM (IEC 61970)
IEC 61850 and PMUs/WANs

## Slide 3: Power Systems Data Formats and System Integration
EMSs long had app-specific, proprietary file formats
  Some crude: column-oriented, fixed width, tab-separated … (similar to FORTRAN)
Deregulation pushing vendors, utilities, etc from doing own custom software and data formats
  Interoperability is key in the evolving EMS world
Problems arise
  Sharing data between differnet vendors/utilities’ SW
  Sharing data even between two versions of same SW

## Slide 4: Solution possibilities
Maintain multiple copies of same data in multiple formats
Store the data in a format compatible with every piece of SW
  Have to remove app-specific data & lose precision
Store data in single, highly-detailed format and create SW to convert to app-specific formats
Use highly detailed format compatible w/every app
#3 and #4 don’t require separate copies but don’t lose precision
#4 is ideal solution

## Slide 5: Data management in then grid
#4: Use highly detailed format compatible w/every app
Requirements for this to work
Highly detailed model to describe the power system
File format capable of storing extended data without affecting the core data
Power system SW vendors and utilities adopt and embrace the data model
CIM can do #1
XML with RDF can do #2

## Slide 6: Today’s Content
Background
UML
XML
RDF
CIM (IEC 61970)
IEC 61850 and PMUs/WANs

## Slide 7: Unified Modeling Language (UML)
Used for modeling wide variety of SW components
  Data structures
  System interactions
  Use cases
Not tied to any one implementation technology: realizeable on multiple platforms
Widely used outside the electricity sector
Standardized by the Object Management Group (OMG), which largely does middleware

## Slide 8: Classes
Class represents specific type of “object” being modeled
Class hierarchy is an abstract model: defines every type of component within a system as a separate class
Very similiar to objected-oriented programming languages: Smalltalk, C++, Java, C#. …
Each UML class can have
  Its own internal attributes
  Relationships with other classes

## Slide 9: Example Circle class
Each instance has its own copy of the data
Useful to have more kinds of data than just a circle!

## Slide 10: Inheritance
Inheritance (AKA generalization) defines class and sub-class relationships
  Sub-classes inherit attributes from parent class (and up)
Kids of classes
  Concrete: can instantiate instances
  Abstract: can’t instantiate instances, use as common parent class for other classes
E.g. Shape class hierarchy (abstract class)
  Circle
  Triangle
  Rectangle
    Square
UML inheritance: clear triangle on parent side of line

## Slide 11: Inheritance (cont.)

## Slide 12: Association
Relationships other than parent-child are useful!
E.g., a Shape can have a Style
UML depiction: a line with role and cardinality at each end
  A Shape has a role Style with cardinality 1
  A Style has a role Shapes with cardinality 0..*
Implications: subclasses of Shape
  Must all have a Style
  Different instances may share or have a different Style
(… below this as in previous slides … )

## Slide 13: Aggregation
A special kind of association, indicating one is a container of instances of the other
UML depiction: a line with
  a clear diamond on the container end
  with role & cardinality at each end
Clear diamond: If the container is destroyed, the contained objects still exist
Example: a Layer that contains Shape objects and can be toggled on and off

## Slide 14: Composition
Specialized form of aggregation: contained object is fundamental part of the container object
  If container destroyed then contained objects are
  E.g., an Anchor class to show where a line can be attached (anchored) on a Shape
UML depiction: filled diamond on the container end

## Slide 15: Final example
Adding a new class, Connection, to represent the connection between two Anchor objects
  Two associations from Connection to the same class (Anchor)!
  But different role names on each end
    FromAnchor, ToAnchor
    FromConnections, ToConnections

## Slide 16: UML for Final Example

## Slide 17: UML Discussion
In programming languages, what is the difference between a procedure/routine and an object?
What two things does an OO language have that UML does not, and why?

## Slide 18: Today’s Content
Background
UML
XML
RDF
CIM (IEC 61970)
IEC 61850 and PMUs/WANs

## Slide 19: Extensible Markup Language (XML)
Markup language (based on SGML, like HTML)
  Defining a set of rules for encoding documents/data
  Both human-readable and machine-readable
Design goals: simplicity, generality, and usability over the Internet
Element expressed as either
  <tag> … contained data … </tag>
  <tag/>
Entry can contain attributes, either
  <tag attributeOne=“how” attributeTwo=“why”/>
  <tag attributeOne=“how” attributeTwo=“why”/>…</tag>
Above, anything in the “…” is a child of the parent
Also, “tag” is NOT a keyword – you’re defining it!

## Slide 20: Simple XML Example: Book
<book title=“Hi” author=“Joe”>
<rev num=“2”>
<year>2006</year>
<month>January</month>
<day>1</day>
</rev>
<chapter title=“Preface”>
<paragraph> …. </paragraph>
….
</chapter>
…. (another chapter)
</book>

## Slide 21: XML Schema
XML per se has no set syntax or semantics for a tag etc
  Apps have to know this to be able to parse and then interpret an XML document
  A schema expresses this
XML Schema Definition (XSD) defines
  Elements and attributes that may appear in a doc
  Parent-child relationships
  #children allowed for an element
  Whether an element can include text
  Data types for elements and attributes
  If data items have fixed values or default values

## Slide 22: Today’s Content
Background
UML
XML
RDF
CIM (IEC 61970)
IEC 61850 and PMUs/WANs

## Slide 23: Resource Description Framework (RDF)
XML so far only has parent-child links
RDF generalizes this
  Element can be assigned a unique ID attribute
  E.g., for a book, sequel and sequelTo elements

## Slide 24: RDF Schema (RDFS)
RDF can express relationships between resources
RDF can’t define a vocabulary for them
RDF Vocabulary Description Language AKA RDFS
RDF Schema
  Does not provide vocabulary for specific resources or classes
  Does allow description of how classes and properties should be used together
  Basically provides a type system for RDF
  E.g.
    lib:book.title used to describe a lib:book
    lib:book.sequel is an element of lib:book and refers to another lib:book entry

## Slide 25: Today’s Content
Background
UML
XML
RDF
CIM (IEC 61970)
IEC 61850 and PMUs/WANs

## Slide 26: CIM
Implementation-agnostic model for defining in UML data used by electric utilities
Example: a Breaker (very common grid component)
  Mechanical switching device capable of making, carrying, and breaking currents under normal circuit conditions
  Making, carrying for a specified time, and breaking current under specified abnormal circuit conditions

## Slide 27: CIM Breaker Example
IdentifiedObject: root class
PowerSystemResource: any resource in a grid
Equipment: a physical device (electrical or mechanical)
ConductingEquipment: carry current or are conductively connected to network
Switch: device that opens+closes
ProtectedSwitch: operated by protection equipment
Breaker: also has a transit time

## Slide 28: Subclasses of Switch

## Slide 29: Today’s Content
Background
UML
XML
RDF
CIM (IEC 61970)
IEC 61850 and PMUs/WANs

## Slide 30: Review of IEC 61850: The Good, the Bad and the Ugly
Designed for substation automation (see Prof. Hauser’s slides for Segment 2)
Main features (from Wikipedia):
  Data Modeling
  Reporting Schemes — server-client relationship which can be triggered based on pre-defined trigger conditions.
  Fast Transfer of events — Generic Substation Events (GSE) GOOSE & GSSE.
  Setting Groups — The setting group control Blocks (SGCB) for config
  Sampled Data Transfer —
  Commands — Various command types to maniuplate sub. Equip.
  Data Storage — Substation Configuration Language (SCL) is defined for complete storage of configured data of the substation in a specific format.

## Slide 31: IEC 61850: For More Info
Wikipedia http://en.wikipedia.org/wiki/61850
Great detailed slide set: http://seclab.web.cs.illinois.edu/wp-content/uploads/2011/03/iec61850-intro.pdf includes some UML
  WAN and other limitations not addressed here…

## Slide 32: The Good
HUGE benefit compared to wires in substation
  Hard to overstate this benefit!
Data model elegant
Substation Configuration Language (SCL) elegant

## Slide 33: The Bad
Complexity
  Far more complex than it has to be given the problem it is tackling
  Double the size/bandwidth of IEEE C37.118 with no extra useful info
  Feels to me like a spec doc by a 1975 Mechanical Engineer specifying HW not a 1995 (or later) SW Engineer specifying SW
Hype
  Almost sounds like it will cure cancer at times
    PJM engineer: 4 substations (ISO has ~30% of the USA footprint)

## Slide 34: The Bad (cont.)
Performance
  Subscriber apps have to be able to detect missing and duplicates (no sophisticated fault-tolerant multicast) when not using TCP via MMS
  GOOSE authentication via RSA signatures: way too expensive for many embedded devices
    UIUC paper (Jaianqing Zhang and Carl Gunter, IEEE SmartGridComm 2010)
    WSU paper (Hauser et al paper from HICSS 45 (2012))
  GOOSE messages very CPU-intesive with ASN.1 integer fields etc, expensive for many embedded devices
  Have to be careful that the multicast (Ethernet broadcast) does not overload small embedded devices (easy to do)
  Messages sent more than once to ensure they get there
    Have to, if no real guarantees provided by communications system!
    But yet more spamming of small embedded devices 

## Slide 35: The Bad (cont.)
Misc
  $3K just to read the spec
  Design by Committee before Full Implementation
    Way better way: IETF and OMG
      David Clark, Internet pioneer
            "We reject: kings, presidents, and voting.
            We believe in: rough consensus and running code"
      Richard Schantz, (IMO) father of middleware
            “Any time you standardize beyond the state of the practice you are in trouble”

## Slide 36: The Bad (cont.)
Misc (cont.)
  PMUs often need many:one (to a PDC) not 1:many communication
  Lack of a reference implementation and reference test suite
    Standard so huge many vendors don’t implement all of it; most vendors violate the standard in some way
    Have to test devices pairwise

## Slide 37: The Ugly
WANs are very different from LANs: partial failures & widely-varying performance (incl. network jitter)
61850 assumes the same interface for a LAN will magically work in a WAN
  Known by distributed computing practitioners and applied researchers to be false since <= 1990
    See the “A Note on Distributed Computing” by Waldo et al 1994

## Slide 38: The Ugly (cont.)
61850-90-5 is the WAN extension
  Advanced multicast is hard, fault-tolerant is harder, real-time is harder yet, with security (not ruining performance and availability) harder still
  Wide range of properties any given implementation could trade off, including latency, jitter, consistency, throughput, resource consumption, availability, ...
  Dec 2010 draft says communications redundancy is crucial
  But the draft has less than one page on it (Sec 8.8) that has no meaningful details
    IETF RFC 2991 it relies on has nothing about end-to-end latency, availability, exploiting a more controllable utility infrastructure, properties above, tradeoffs below (next slide), etc
  Integration with IP Multicast (a common underlying 1:many transport, which BTW provides no reliability guarantees) is undefined
  Integration with MPLS (a common “QoS”-like service) is undefined

## Slide 39: The Ugly (cont.)
61850-90-5 WAN extension (cont.)
  Do implementers (or drafters) know this space of possible properties, what tradeoffs their given implementations make? Very unlikely…
  Do utilities/ISOs know what tradeoffs they are being sold, and how appropriate they are for them? Unlikelier!
Bottom line: a lead control engineer from a large utility to me
  2009: “No way in hell am I letting 61850 outside my substations”
  2011: (ruefully) “I was overruled from above, because its ‘a standard’.”
    But a standard for doing what?
      Certainly not, IMO, WAN communication, at least by any competent distributed computing expert!
    With what properties traded off?